## Sheet1
Air Filtration Testing of Mogul Products at Blue Heaven ASHRAE 52.2 flat Sheet | [7 empty] | EN779 |  |  |  |  | Mogul Products at Blue Heaven ISO 16890
Test Item | Blue Heaven Sample No. | 0.3 to 1 micron E1 (%) | 1.1 to 2.6 micron E2 (%) | 3.5 to 8.5 microns E3 (%) | Estimated MERV | Resistance ("H2O") at 10 FPM | Pa | Rating | Initial Efficiency (%) at 0.4 microns | Resistance ("H2O") at 10 FPM | Resistance Pa |  | ISO 16890 will replace EN779 beginning in 2017. It shifts emphasis from filtration performance to classes of particle matter size (PM) which are used as evaluation parameters by the World Health Organization(WHO). Additionally, filters are treated with IP alcohol to discharge any charge and the difference reported. Usually no change unless corona charged.
Reemay 2040 | 16-0625 | 3 | 8 | 58 | 7 | 0.02 | 4.9768 | G4 |  |  |  |  | Test Item | ePM1 (%) | ePM2.5 % | ePM10 % | Resistance ("H2O") at 10 FPM | Pa
Mogul 135 TCS-2 (0.75mm) Current Product | 16-2013 | 21 | 29 | 70 | 8 | 0.023 | 5.7233 | G4 |  |  |  |  | Mogul 135 TCS-2 (0.75mm) Current Product | 23 | 25 | 48 | 0.02 | 4.9768
Mogul 135 TCS-3 (0.53mm) Premium Product | 16-2015 | 48 | 54 | 84 | 10 | 0.02 | 4.9768 | M5 |  |  |  |  | Mogul 135 TCS-3 (0.53mm) Premium Product | 5 | 10 | 56 | 0.07 | 17.4188
Mogul 180 gsm TCS-2 Current Product | 16-2014 | 32 | 40 | 78 | 9 | 0.025 | 6.221 | M5
Mogul 100 gsm TCS-2 Current Product | 16-2012 | 19 | 22 | 58 | 7 | 0.014 | 3.4838 | G4
Mogul 80 gsm TCS-2 Current Product | 16-2011 | 24 | 27 | 54 | 7 | 0.012 | 2.9861 | G4
Mogul 68 gsm TCS -2 Current Product | 16-2010 | 21 | 26 | 52 | 7 | 0.011 | 2.7372 | G4
Durell Cross Lapped 70 gsm 100% PES | 17-159-2-3-4 | 21 | 29 | 66 | 7 | 0.02 | 4.9768 | G4
Durell Cross Lapped 100 gsm 100% PES | 17-159-8-10 | 26 | 35 | 74 | 8 | 0.023 | 5.7233 | G4
Durell Cross Lapped 150 gsm 100% PES | 16-2152 | 9 | 39 | 92 | 9 | 0.13 | 32.3492 | M5
Durell Cross Lapped 200 gsm 100% PES | 16-2153 | 20 | 58 | 99 | 10 | 0.24 | 59.7216 | M5
Madaline 80 gsm | 17-159-5-6-7 | 60 | 77 | 92 | 11 | 0.11 | 27.3724 | M6
Madaline 100 gsm | 17-031-1 | 80 | 93 | 99 | 14 | 0.2 | 49.768 | F8
Madaline 120 gsm | 17-031-2 | 84 | 96 | 100 | 14 | 0.32 | 79.6288 | F8
Mogul Thermal Calendered 82 gsm Meltblown | 16-2016 | 56 | 80 | 99 | 12 | 0.075 | 18.663 | M6
Mogul Thermal Calendered 100 gsm Meltblown | 17-086-1 | 48 | 80 | 100 | 12 | 0.11 | 27.3724 | M6
Mogul Thermal Calendered 20 gsm Meltblown | 17-320-1 | Tested as EN779 | [5 empty] | M5 | 10.14 | 0.05 | 12
Mogul Thermal Calendered 40 gsm Meltblown | 17-320-2 | Tested as EN779 | [5 empty] | M6 | 22.32 | 0.085 | 21
Mogul Thermal Calendered (2) Layers 20 gsm Meltblown | 17-320-3 | Tested as EN779 | [5 empty] | M6 | 27.4 | 0.1 | 25
Mogul Thermal Calendered 20 & 40 gsm Meltblown |  | Tested as EN779 | [5 empty] | F7 | 35.44 | 0.15 | 37
Spunlace 50gsm 60/40 PES/Viscose Light Vac. Dep. Al coating | 17-111-1 | 57 | 62 | 80 | 10 | 0.01 | 2.4884 | M5 |  |  |  | Vacuum Deposition
Spunlace 50gsm 60/40 PES/Viscose Heavy Vac. Dep. Al coating | 17-111-2 | 35 | 36 | 56 | 7 | 0.01 | 2.4884 | G4 |  |  |  | Vacuum Deposition
Mogul 120 gsm PET Bico Spunbond/ PBT, 1,475+0,59+1,475 Composite | 16-0624 | 65 | 90 | 100 | 13 | 0.135 | 33.5934 | F7
| Flat Sheet, 16 x 16 inches, Flow 10 FPM/5.1cm/s | [6 empty] | Flow - 10.5 FPM/5.3 cm/s